## Ventilation
Example of tags and additional information to be mapped to RealEstateCore |  |  | n/a= | not available
Example: Building no: 98765 | AHU010 is placed in room 1265 in building D
Description | Tag, unique ID from legacy system | Log intervall | Type | What is measured? | Unit | Placed in room | Placement type | Serves | Served By
AHU | 98765-D-LB010 | n/a | n/a | n/a | n/a | 1265 | n/a | Section A part of Building D | KB010;VS010
TemperatureSensor Supply air | 98765-D-LB010-GT11 | 10 min | Sensor | Temperature | °C | 1265 | supply air | Section A part of Building D | n/a
Calculated actual valuesupply air Temperature | 98765-D-LB010-GT11_BB | 10 min | Sensor | Temperature | °C | 1265 | n/a | Section A part of Building D | n/a
Setpoint supply air Temperature | 98765-D-LB010-GT11_BV | 10 min | Sensor | Temperature | °C | 1265 | n/a | Section A part of Building D | n/a
TemperatureSensor supply air | 98765-D-LB010-GT41 | 10 min | Sensor | Temperature | °C | 1265 | supply air | Section A part of Building D | n/a
TemperatureSensor extract air | 98765-D-LB010-GT42 | 10 min | Sensor | Temperature | °C | 1265 | Extract air | Section A part of Building D | n/a
TemperatureSensor exhaust air | 98765-D-LB010-GT43 | 10 min | Sensor | Temperature | °C | 1265 | Exhaust air | Section A part of Building D | n/a
TemperatureSensor intake air | 98765-D-LB010-GT31 | 10 min | Sensor | Temperature | °C | 1265 | Outdoor air | Section A part of Building D | n/a
TemperatureSensor room | 98765-D-LB010-GT32 | 10 min | Sensor | Temperature | °C | 1043 | Room | Section A part of Building D | n/a
Presence Sensor room | 98765-D-LB010-GX81 | 1 min | Sensor | Presence | 0/1 | 1043 | Room | Section A part of Building D | n/a
FrostSensor heating circuit | 98765-D-LB010-GT81 | 10 min | Sensor | Temperature | °C | 1265 | Secondary circuit | Section A part of Building D | n/a
TemperatureSensor recycling | 98765-D-LB010-GT21 | 10 min | Sensor | Temperature | °C | 1265 | Recyckling | Section A part of Building D | n/a
supply air Pressure | 98765-D-LB010-GP11 | 10 min | Sensor | Pressure | Pa | 1265 | supply air | Section A part of Building D | n/a
Setpoint supply air Pressure | 98765-D-LB010-GP11_B | 10 min | Set point | Pressure | Pa | 1265 | n/a | Section A part of Building D | n/a
Extract air Pressure | 98765-D-LB010-GP12 | 10 min | Sensor | Pressure | Pa | 1265 | Extract air | Section A part of Building D | n/a
Setpoint extract air Pressure | 98765-D-LB010-GP12_B | 10 min | Set point | Pressure | Pa | 1265 | n/a | Section A part of Building D | n/a
supply air Flow | 98765-D-LB010-GF41 | 10 min | Sensor | Flow | m³/s | 1265 | supply air | Section A part of Building D | n/a
Extract air Flow | 98765-D-LB010-GF42 | 10 min | Sensor | Flow | m³/s | 1265 | Extract air | Section A part of Building D | n/a
Fan coil supply air Actuator | 98765-D-LB010-TF1 | 10 min | Actuator | n/a | % | 1265 | n/a | Section A part of Building D | n/a
Fan coil extract air Actuator | 98765-D-LB010-FF1 | 10 min | Actuator | n/a | % | 1265 | n/a | Section A part of Building D | n/a
State extract air fan coil | 98765-D-LB010-FF1_D | 10 min | Sensor | State | 0/1 | 1265 | Extract air | Section A part of Building D | n/a
State supply air fan coil | 98765-D-LB010-TF1_D | 10 min | Sensor | State | 0/1 | 1265 | supply air | Section A part of Building D | n/a
Operational Time AHU | 98765-D-LB010-DT | 1h | Sensor | Time | h | 1265 |  | Section A part of Building D | n/a
Outdoor air dampfer state open | 98765-D-LB010-ST21_IÖ | 10 min | Sensor | State | 0/1 | 1265 | Outdoor air | Section A part of Building D | n/a
Outdoor air dampfer state closed | 98765-D-LB010-ST21_IS | 10 min | Sensor | State | 0/1 | 1265 | Outdoor air | Section A part of Building D | n/a
Extract air dampfer state open | 98765-D-LB010-ST22_IÖ | 10 min | Sensor | State | 0/1 | 1265 | Exhaust air | Section A part of Building D | n/a
Extract air dampfer state closed | 98765-D-LB010-ST22_IS | 10 min | Sensor | State | 0/1 | 1265 | Exhaust air | Section A part of Building D | n/a
Rotating recycling Actuator | 98765-D-LB010-RÅ01 | 10 min | Actuator | n/a | % | 1265 | n/a | Section A part of Building D | n/a
State pump heating circuit | 98765-D-LB010-PV01_D | 10 min | Sensor | State | 0/1 | 1265 | n/a | Section A part of Building D | n/a
State cooling circuit | 98765-D-LB010-PK01_D | 10 min | Sensor | State | 0/1 | 1265 | n/a | Section A part of Building D | n/a
Heating valve Actuator | 98765-D-LB010-SV21 | 10 min | Actuator | n/a | % | 1265 | Heating circuit | Section A part of Building D | n/a
Cooling valve Actuator | 98765-D-LB010-SV41 | 10 min | Actuator | n/a | % | 1265 | Cooling circuit | Section A part of Building D | n/a
Specific Fan Power | 98765-D-LB010-SFP | 1h | Calculated actual value | Power/Flow | kW/(m³/s) | 1265 | n/a | Section A part of Building D | n/a

## Heating
|  |  | n/a= | not available
Example: Building no: 98765 | Heating central is placed in utilitiy room 1163 in building D
Description | Tag, unique ID from legacy system | Log intervall | Type | What is measured? | Unit | Placed in room | Placement type | Serves | Served By
Heating system | 98765-D-VS010 | n/a | n/a | n/a | n/a | 1163 | n/a | Building D | VP010
Hot drinking water system | 98765-D-VV010 | n/a | n/a | n/a | n/a | 1163 | n/a | Building D | VP010
Temperaturee sensor hotwater supply | 98765-D-VV010-GT11 | 5 min | Sensor | Temperature | °C | 1163 | Supply hot water | Building D | n/a
Set point hot water supply | 98765-D-VV010-GT11_B | 10 min | Set point | Temperature | °C | 1163 | n/a | Building D | n/a
TemperatureSensor hotwater supply | 98765-D-VV010-GT12 | 5 min | Sensor | Temperature | °C | 1163 | Supply hot water | Building D | n/a
Set point hot water supply | 98765-D-VV010-GT12_B | 10 min | Set point | n/a | °C | 1163 | n/a | Building D | n/a
Hot water Actuator | 98765-D-VV010-SV21 | 10 min | Actuator | n/a | % | 1163 | Hot water circuit | Building D | n/a
Hot water Actuator mixing valve | 98765-D-VV010-SV71 | 10 min | Actuator | n/a | % | 1163 | Hot water circuit | Building D | n/a
TemperatureSensor hotwater return | 98765-D-VC010-GT41 | 5 min | Sensor | Temperature | °C | 1163 | Hot water circulation | Building D | n/a
State valve hot water circulation | 98765-D-VC010-PV01_D | 10 min | Sensor | State | 0/1 | 1163 | Hot water circulation | Building D | n/a
TemperatureSensor heating supply | 98765-D-VS010-GT11 | 10 min | Sensor | Temperature | °C | 1163 | Supply heating | Building D | n/a
Caculated Set point Temperature supply | 98765-D-VS010-GT11_BB | 10 min | Set point | n/a | °C | 1163 | n/a | Building D | n/a
Set point supply Temperature | 98765-D-VS010-GT11_BV | 10 min | Set point | n/a | °C | 1163 | n/a | Building D | n/a
Heating valve Actuator | 98765-D-VS010-SV21 | 10 min | Actuator | n/a | % | 1163 | Heating | Building D | n/a
State valve heating | 98765-D-VS010-PV01_D | 10 min | Sensor | State | 0/1 | 1163 | Heating | Building D | n/a
DifferentialPressure Sensor heating | 98765-D-VS010-GP11 | 10 min | Sensor | Pressure | Pa | 1163 | Heating | Building D | n/a
Supply Sensor temperature district heating | 98765-D-VP010-GT41 | 10 min | Sensor | Temperature | °C | 1163 | Supply district hetaing | Building D | n/a
Return Sensor temperature district heating | 98765-D-VP010-GT41 | 10 min | Sensor | Temperature | °C | 1163 | Return district heating | Building D | n/a

## Cooling
|  |  | n/a= | not available
Example: Building no: 98765 | Cooling central is placed in utilitiy room 1164 in building D
Description | Tag, unique ID from legacy system | Log intervall | Type | What is measured? | Unit | Placed in room | Placement type | Serves | Served By
Cooling circuit | 98765-D-KB010 | n/a | n/a | n/a | n/a | 1164 | n/a | Building D | KP010
Temperature sensor Cooling circuit supply | 98765-D-KB010-GT11 | 10 min | Sensor | Temperature | °C | 1164 | Supply Cooling circuit | Building D | n/a
Calculated set point supply temperature | 98765-D-KB010-GT11_BB | 10 min | Set point | Temperature | °C | 1164 | n/a | Building D | n/a
Setpoint supply temperature | 98765-D-KB010-GT11_BV | 10 min | Set point | Temperature | °C | 1164 | n/a | Building D | n/a
Cooling circuit valve actuator | 98765-D-KB010-SV21 | 10 min | Actuator | n/a | % | 1164 | Cooling circuit | Building D | n/a
State pump Cooling circuit | 98765-D-KB010-PK01_D | 10 min | Sensor | State | 0/1 | 1164 | Cooling circuit | Building D | n/a
Differential pressure sensor Cooling circuit | 98765-D-KB010-GP11 | 10 min | Sensor | Pressure | Pa | 1164 | Cooling circuit | Building D | n/a
Supply sensor temperature Cooling circuit | 98765-D-KP010-GT41 | 10 min | Sensor | Temperature | °C | 1164 | Supply district cooling | Building D | n/a
Return sensor temperature Cooling circuit | 98765-D-KP010-GT41 | 10 min | Sensor | Temperature | °C | 1164 | Return district cooling | Building D | n/a

## Room control
|  |  | n/a= | not available
Example: Building no: 98765 | All rooms are placed in building D
Description | Tag, unique ID from legacy system | Log intervall | Type | What is measured? | Unit | Placed in room | Serves | Placement type
Temperature sensor room | 98765-D-4611-GT31 | 10 min | Sensor | Temperature | °C | 4611 | 4611 | Wall in room
Set point temperature | 98765-D-4611-GT31_B | 10 min | Set point | Temperature | °C | 4611 | 4611 | n/a
Presence sensor room | 98765-D-4611-GX81 | 1 min | Sensor | Presence | 0/1 | 4611 | 4611 | Wall in room
CO2 sensor room | 98765-D-4611-GX11 | 10 min | Sensor | CO2 | ppm | 4611 | 4611 | Wall in room
Set point CO2 room | 98765-D-4611-GX11_B | 10 min | Set point | Temperature | ppm | 4611 | 4611 | n/a
Heating actuator | 98765-D-4611-SV21 | 10 min | Actuator | n/a | % | 4611 | 4611 | Radiator
Cooling actuator | 98765-D-4611-SV41 | 10 min | Actuator | n/a | % | 4611 | 4611 | Cooling radiator in ceiling
Ventilation dampfer actuator | 98765-D-4611-ST41 | 10 min | Actuator | n/a | % | 4611 | 4611 | Supply air
Temperature sensor room | 98765-D-4612-GT31 | 10 min | Sensor | Temperature | °C | 4612 | 4612 | Wall in room
Set point temperature | 98765-D-4612-GT31_B | 10 min | Set point | Temperature | °C | 4612 | 4612 | n/a
Presence sensor room | 98765-D-4612-GX81 | 1 min | Sensor | Presence | 0/1 | 4612 | 4612 | Wall in room
CO2 sensor room | 98765-D-4612-GX11 | 10 min | Sensor | CO2 | ppm | 4612 | 4612 | Wall in room
Set point CO2 room | 98765-D-4612-GX11_B | 10 min | Set point | Temperature | ppm | 4612 | 4612 | n/a
Heating actuator | 98765-D-4612-SV21 | 10 min | Actuator | n/a | % | 4612 | 4612 | Radiator
Cooling actuator | 98765-D-4612-SV41 | 10 min | Actuator | n/a | % | 4612 | 4612 | Cooling radiator in ceiling
Ventilation dampfer actuator | 98765-D-4612-ST41 | 10 min | Actuator | n/a | % | 4611 | 4612 | Supply air
Temperature sensor room | 98765-D-4613-GT31 | 10 min | Sensor | Temperature | °C | 4613 | 4613 | Wall in room
Set point temperature | 98765-D-4613-GT31_B | 10 min | Set point | Temperature | °C | 4613 | 4613 | n/a
Presence sensor room | 98765-D-4613-GX81 | 1 min | Sensor | Presence | 0/1 | 4613 | 4613 | Wall in room
CO2 sensor room | 98765-D-4613-GX11 | 10 min | Sensor | CO2 | ppm | 4613 | 4613 | Wall in room
Set point CO2 room | 98765-D-4613-GX11_B | 10 min | Set point | Temperature | ppm | 4613 | 4613 | n/a
Heating actuator | 98765-D-4613-SV21 | 10 min | Actuator | n/a | % | 4613 | 4613 | Radiator
Cooling actuator | 98765-D-4613-SV41 | 10 min | Actuator | n/a | % | 4613 | 4613 | Cooling radiator in ceiling
Ventilation dampfer actuator | 98765-D-4613-ST41 | 10 min | Actuator | n/a | % | 4613 | 4613 | Supply air
Temperature sensor room | 98765-D-4612-GT31 | 10 min | Sensor | Temperature | °C | 5321 | Zon1 | Wall in room
Set point temperature | 98765-D-4612-GT31_B | 10 min | Set point | Temperature | °C | 5321 | Zon1 | n/a
Presence sensor room | 98765-D-4612-GX81 | 1 min | Sensor | Presence | 0/1 | 5321 | Zon1 | Wall in room
CO2 sensor room | 98765-D-4612-GX11 | 10 min | Sensor | CO2 | ppm | 5321 | Zon1 | Wall in room
Set point CO2 room | 98765-D-4612-GX11_B | 10 min | Set point | Temperature | ppm | 5321 | Zon1 | n/a
Heating actuator | 98765-D-4612-SV21 | 10 min | Actuator | n/a | % | 5323 | Zon1 | Radiator
Cooling actuator | 98765-D-4612-SV41 | 10 min | Actuator | n/a | % | 5323 | Zon1 | Cooling radiator in ceiling
Ventilation dampfer actuator | 98765-D-4612-ST41 | 10 min | Actuator | n/a | % | 5321 | Zon1 | Supply air

## Rooms
|  |  | n/a= | not available
Example: Building no: 98765 | All rooms are placed in building D
Description | Room number | ServedBy Ventilation | ServedBy Heating | ServedBy Cooling | BIM reference (if existing)
Driftutrymme | 1265 | LB010 | VS010 | n/a | [IFC GUID]
Driftutrymme | 1163 | LB010 | VS010 | n/a
Driftutrymme | 1164 | LB010 | VS010 | n/a
Kontor | 4611 | LB010 | VS010 | KB010
Mötesrum | 4612 | LB010 | VS010 | KB010
Kontor | 4613 | LB010 | VS010 | KB010
Öppet landskap | 5321 | LB012 | VS010 | KB010

## Meters
Example: Building no: 98765 | Meters are placed in utility room 1163 in building D
Description | Tag, unique ID from legacy system | Log intervall | Type | What is measured? | Unit | Placed in room | Placement type | Serves | Served By
Electricity active Energy | 98765-D-… | 60 min | Sensor | Energy | kWh | 1163 | Intake, Photo voltaic, tenant, EV chargers, battary, … | Building D
Electricity momentary Power | 98765-D-… |  | Sensor | Power | kW | 1163 |  | Building D
Electricity Voltage L1-N | 98765-D-… |  | Sensor | Voltage | V | 1163 |  | Building D
Electricity Voltage L2-N | 98765-D-… |  | Sensor | Voltage | V | 1163 |  | Building D
Electricity Voltage L3-N | 98765-D-… |  | Sensor | Voltage | V | 1163 |  | Building D
Electricity Current L1 | 98765-D-… |  | Sensor | Current | A | 1163 |  | Building D
Electricity Current L2 | 98765-D-… |  | Sensor | Current | A | 1163 |  | Building D
Electricity Current L3 | 98765-D-… |  | Sensor | Current | A | 1163 |  | Building D
Electricity Cos-fi active L1 | 98765-D-… |  | Sensor | Cos phi |  | 1163 |  | Building D
Electricity Cos-fi active L2 | 98765-D-… |  | Sensor | Cos phi |  | 1163 |  | Building D
Electricity Cos-fi active L3 | 98765-D-… |  | Sensor | Cos phi |  | 1163 |  | Building D
Electricity Frequency | 98765-D-… |  | Sensor | Frequency | Hz | 1163 |  | Building D
District heating Energy | 98765-D-… | 60 min | Sensor | Energy | kWh | 1163 |  | Building D
District heating Flow | 98765-D-… |  | Sensor | Flow | l/s | 1163 |  | Building D
District heating supply Temperature | 98765-D-… |  | Sensor | Temperature | C | 1163 |  | Building D
District heating return Temperature | 98765-D-… |  | Sensor | Temperature | C | 1163 |  | Building D
Secondary heating Energy | 98765-D-… | 60 min | Sensor | Energy | kWh | 1163 |  | Building D
Secondary heating Flow | 98765-D-… |  | Sensor | Flow | l/s | 1163 |  | Building D
Secondary heating supply Temperature | 98765-D-… |  | Sensor | Temperature | C | 1163 |  | Building D
Secondary heating return Temperature | 98765-D-… |  | Sensor | Temperature | C | 1163 |  | Building D
District cooling Energy | 98765-D-… | 60 min | Sensor | Energy | kWh | 1163 |  | Building D
District cooling Flow | 98765-D-… |  | Sensor | Flow | l/s | 1163 |  | Building D
District cooling supply Temperature | 98765-D-… |  | Sensor | Temperature | C | 1163 |  | Building D
District cooling return Temperature | 98765-D-… |  | Sensor | Temperature | C | 1163 |  | Building D
Secondary cooling Energy | 98765-D-… | 60 min | Sensor | Energy | kWh | 1163 |  | Building D
Secondary cooling Flow | 98765-D-… |  | Sensor | Flow | l/s | 1163 |  | Building D
Secondary cooling supply Temperature | 98765-D-… |  | Sensor | Temperature | C | 1163 |  | Building D
Secondary cooling return Temperature | 98765-D-… |  | Sensor | Temperature | C | 1163 |  | Building D
Water volume | 98765-D-… | 60 min | Sensor | Volume | m3 | 1163 |  | Building D
Water Flow | 98765-D-… |  | Sensor | Flow | l/s | 1163 |  | Building D
Drinking water volume | 98765-D-… |  | Sensor | Volume | m3 | 1163 |  | Building D
Drinking water flow | 98765-D-… |  | Sensor | Flow | l/s | 1163 |  | Building D
Drinking hot water volume | 98765-D-… |  | Sensor | Volume | m3 | 1163 |  | Building D
Drinking hot water flow | 98765-D-… |  | Sensor | Flow | l/s | 1163 |  | Building D
Drinking hot water temperature | 98765-D-… |  | Sensor | Temperature | C | 1163 |  | Building D